## Feed Calculator for STPs
Simmonds & Bristow STP Feeding Tool
Input Instructions: Fill all Blue Cells below with site specific values or an approximation based on the typical ranges provided. Design specifications should be detailed in the STP O&M Manual under Design Specifications or Influent Characteristics. |  |  |  |  | Output Instructions: Select a Fertiliser Combination and a Carbohydrate Source and take note of the Orange cells below designating the day, month and quarterly values provided for daily dosing and bulk ordering. |  |  |  | Design Variables: These values list the current elemental ratios compared to theory and the basic fertiliser values used to calculate dosing rates.
Feed Calculator for STPs |  |  | Typical Range |  | Fertiliser: | DAP + (UREA OR BIG N) |  |  | Ratio | C | N | P
[5 empty] | Chemical | kg/day | ~kg/month | ~kg/quarter | Current | 30 | 6 | 1
Design Flow Rate | 400 | m3/day | - | - | DAP | 4.28 | 128.4 | 385.2 | Terry's Design | 100 | 5 | 1
Design BOD | 300 | mg/L | 200 | 300 | UREA | 9.4904 | 284.713 | 854.1391
Design Ammonia (As N) | 60 | mg/L | 40 | 85 | OR BIG N | 5.3239 | 159.7171 | 479.1512 |  | Nutrients
Design Phosphorus | 10 | mg/L | 6 | 20 | OR |  |  |  | Fertiliser | N | P
[6 empty] | MAP + (UREA OR BIG N) |  |  | DAP | 18% | 20%
Design BOD Mass (M) | 120 | kg/day | - | - | Chemical | kg/day | ~kg/month | ~kg/quarter | MAP | 10% | 22%
Design Nitrogen Mass (N) | 24 | kg/day | - | - | MAP | 3.8909 | 116.7273 | 350.1818 | UREA | 46% | 0%
Design Phosphorus Mass (P) | 4 | kg/day | - | - | UREA | 10.3194 | 309.581 | 928.7431 | BIG N | 82% | 0%
[5 empty] | OR BIG N | 5.7889 | 173.6674 | 521.0022
Likely Loading | 80 | ep | - | -
Loading | 180 | L/ep/day | 150 | 300 | Carbohydrate: | White Sugar
Flow Rate | 14400 | L/day | - | - | Chemical | kg/day | ~kg/month | ~kg/quarter
[5 empty] | White Sugar | 30.848 | 956.288 | 2868.864
Turn Down | 27.7778 | to 1 | - | - | OR
60% Sucrose Solution
Minimium Feed Load Ration | 25% |  | 25% | 100% | Chemical | l/day | ~l/month | ~l/quarter
[5 empty] | Sucrose | 38.56 | 1195.36 | 3586.08
Likely Feed Available |  |  |  |  | OR
BOD Mass (M) | 4.32 | kg/day |  |  |  | Refinery Molasses
Nitrogen Mass (N) | 0.864 | kg/day |  |  | Chemical | l/day | ~l/month | ~l/quarter
Phosphorus Mass (P) | 0.144 | kg/day |  |  | Molasses | 57.84 | 1793.04 | 5379.12
Additional Feed Required: | kg/day | kg per month | kg/quarter
BOD Mass (M) | 25.68 | 796.08 | 2388.24 |  | Legend:
Nitrogen Mass (N) | 5.136 | 159.216 | 477.648 |  |  | *Input Required
Phosphorus Mass (P) | 0.856 | 26.536 | 79.608 |  |  | *Output Dosing Requirements
© 2020 Simmonds & Bristow Pty Ltd
Note on C5: Adam Coates: This value should be clearly stated under Design Specifications in the STP O&M Manual.
Note on C6: Adam Coates: This value should be stated under Design Influent Characteristics in the STP O&M Manual.
Note on C7: Adam Coates: This value should be stated under Design Influent Characteristics in the STP O&M Manual. *May be listed as Nitrogen.
Note on C8: Adam Coates: This value should be stated under Design Influent Characteristics in the STP O&M Manual.
Note on C14: Adam Coates: Estimated Site Popluation during low flow period - This value is the likely number of "Equivalent Persons" expected to be present on site during the low occupancy period.
Note on C15: Adam Coates: This value is the expected loading per "Equivalent Person". If the flow rate below is not equivalent to the actual flow rates measured increase Loading value until the flow rate value is equivalent.
Note on C20: Adam Coates: This value is the minimum feed ration as a percentage of the Design Rates. This should be as low as possible within the specific STPs design capabilities. It is the minimum loading required for the STP to function without major issues.